Data sheet

PIKO 5.5

Technical data PIKO 5.5

n 3-phase feed-in

n Transformerless converting

n Integrated electronic DC switch

n Broad input voltage range

n Standard integrated communication package with data logger, web server, solar portal and the following interfaces: 2x Ethernet, RS485, S0, 4x analogue inputs (e.g. for ripple control receivers or PIKO Sensor)

n PIKO BA Sensor can be connected for the measurement of building consumption and for dynamic active power control

n Integrated switch contact for self-consumption optimisation

n Smart Home-ready, EEBus 1.0-ready

| Input side (DC) |  |  |
| --- | --- | --- |
| Max. PV power (cos φ = 1) | kWp | 6.1 |
| Rated input voltage (VDC,r) | V | 680 |
| Max. input voltage (VDCmax) | V | 1000 |
| Min. input voltage (VDCmin) | V | 160 |
| Start-up input voltage (VDCstart) | V | 180 |
| Max. MPP voltage (VMPPmax) | V | 800 |
| Min. MPP voltage for DC rated output in single tracker mode (VMPPmin) | V | 530 |
| Min. MPP voltage for DC rated output in two-tracker mode (VMPPmin) | V | 265 |
| Max. input current (IDCmax) | A | 11 |
| Max. input current with parallel connection (input DC1+DC2) | A | 22 |
| Number of DC inputs |  | 2 |
| Number of independent MPP trackers |  | 2 |
| Output side (AC) |  |  |
| Rated output, cos φ = 1 (PAC,r) | kW | 5.5 |
| Max. output apparent power, cos φ, adj | kVA | 5.5 |
| Max. output voltage (VACmax) | V | 264.5 |
| Min. output voltage (VACmin) | V | 184 |
| Rated output current | A | 8 |
| Max. output current (IACmax) | A | 8 |
| Short-circuit current (peak / RMS) | A | 12.5 / 8.8 |
| Grid connection |  | 3N~, AC, 400 V |
| Rated frequency (fr) | Hz | 50 |
| Max. grid frequency (fmax) | Hz | 51.5 |
| Min. grid frequency (fmin) | Hz | 47.5 |
| Setting range of the power factor cos φ AC,r |  | 0.80…1…0.80 |
| Power factor for rated power (cos φAC,r) |  | 1 |
| Max. total harmonic distortion | % | 3 |
| Device properties |  |  |
| Standby consumption | W | 1,8 |
| Efficiency |  |  |
| Max. efficiency | % | 97.7 |
| European efficiency | % | 96.3 |
| MPP adjustment efficiency | % | 99.9 |
| Warranty |  |  |
| Warranty (years) |  | 5 |
| Warranty extension optional (years) |  | 10 / 20 |

Efficiency characteristics of PIKO 5.5

η [%]

99

98

97                                                                                                                                        VDC,r = 680 V

96                                                                                                                                        VMPPmax = 800 V

Contact                                                           95

VMPPmin

= 265 V

KOSTAL Solar Electric GmbH Hanferstr. 6

79108 Freiburg i. Br. Germany

Tel. +49 761 477 44 - 100

Fax +49 761 477 44 - 111 www.kostal-solar-electric.com

94

93

92

91

90

89

88

87                                                                                                                             Pac

0%              20%               40%               60%                80%             100%   Pac,r

(2 trackers sym)

# Text boxes

| System data |  |  |
| --- | --- | --- |
| Topology: Without galvanic separation - transformerless |  | H |
| Internal protection according to IEC 60529 housing / fan |  | IP 65 / IP 55 |
| Protective class according to IEC 62103 |  | I |
| Overvoltage category according to IEC 60664-1 Input side (PV generator) |  | II |
| Overvoltage category according to IEC 60664-1 Output side (grid connection) |  | III |
| Pollution Degree |  | 4 |
| Environmental category (outdoor installation) |  | H |
| Environmental category (interior installation) |  | H |
| UV resistance |  | H |
| Minimum cable cross-section of AC connecting line | mm² | 1,5 |
| Minimum cable cross-section of DC connecting line | mm² | 4 |
| Max. fusing on output side |  | B16, C16 |
| Operator protection (EN 62109-2) |  | RCCB Typ B |
| Electronic disconnection device integrated |  | H |
| Height | mm | 385 (15.16 in) |
| Width | mm | 500 (19.69 in) |
| Depth | mm | 236 (9.29 in) |
| Weight | kg | 25.5 (56.22 lb) |
| Cooling principle - convection |  | – |
| Cooling principle - regulated fans |  | H |
| Max. air throughput | m³/h | 84 |
| Noise emission | dBA | 52 |
| Ambient temperature | °C | -20…60 (-4...140 °F) |
| Max. installation altitude above sea level | m | 2000 (6562 ft) |
| Relative humidity | % | 4…100 |
| Connection technology at input side - MC 4 |  | H |
| Connection technology at output side - spring-loaded terminal strip |  | H |
| Interfaces |  |  |
| Ethernet RJ45 |  | 2 |
| RS485 |  | 1 |
| S0 |  | 1 |
| Analogue inputs |  | 4 |
| PIKO BA Sensor Interface |  | 1 |

97,7 %   max

07 / 2015 - EN - 10077966

This manual is subject to technical changes and printing errors. You can find current information at www.kostal-solar-electric.com. Manufacturer: KOSTAL Industrie Elektrik GmbH, Hagen, Germany