SOLARFLEX®-X PV1-F

GREEN LINE

The  perfect cable for photovoltaic systems With  our   SOLARFLEX®-X  PV1-F HELUKABEL®    we  offer  a  product   in  our designated Green Line, which is in the scope  of our long lasting commitment to renewable  energies and has TÜV and VDE certifications along with the high- est  quality standards typical for HELUKABEL®  products. The production takes place in our own cable factory in Germany. Therefore we can act flexible, fast and an in a cost-effective manner  to market requirements. Cross-sections from

1 x 2,5  mm²  up  to  1 x 95  mm²  are available from stock. If required  we are able to deliver SOLARFLEX®-X PV1-F up to 1 x 240  mm².  The wire is used glo- bally in stand-alone and networked  systems as a module  or branch  wire. Both insulation  layers are set-off  coloured  from each  other  for improved  handling: black sheathing on natural  colour conductor insulation  in the  standard versi- on, or optionally, red or blue sheathing to simplify local installation.  Twin wire SOLARFLEX®-X PV1-F in cross-sections  from 2 x 2,5 mm² up to 2 x 16 mm² are also available. In addition  we offer pre-assembled cables, connectors and tools for professional assembly of photovoltaic  installations.

Technical Data

• temperature range

-40°C to +90°C

max. temp.  at conductor +120°C

• nominal voltage

according  to VDE U0/U 600/1000 V AC

1800  V DC conductor/conductor

• AC test  voltage 10000  V

• minimum bending radius

fixed installation approx. 10 x outer Ø

flexing (occasional) approx. 4 x cable Ø

Cable structure

• bare copper,  tinned,  finely stranded

• according  to DIN VDE 0295  Class 5 and

IEC 60228  cl.

• double-insulated

• Insulation cross-linked Polyolefin

• outer sheath  cross-linked Polyolefin

• sheath  colours: black, red, blue

Properties

• approval: VDE (Reg. 8266),  TÜV

(2 PfG 1169/08.2007, R60025298),

UL on request,  RoHS and CE compliant

According to PV1-F requirement profile for

PV cables DKE/VDE AK 411.2.3

• ozone resistant acc. to EN 50396

• weather  and UV resistant acc. to HD 605/A1

• halogen-free acc. to EN 50267-2-1,

EN 60684-2

• resistant to acid and bases acc. to

EN 60811-2-1

• flame-resistant  according  to

VDE 0482-332-1-2, DIN EN 60332-1-2,

IEC 60332-1

• very robust  and abraison-resistant sheath

acc. to DIN EN 53516

• resistant to short-circuits up to 200°C thanks

to their double insulation; short-circuits

temperature 200°C / 5 sec.

• anticipated service life - 25 years

• hydrolysis and ammoniac  resistant

Notes

• version with UL approval on request

• version with rodent protection available

• all types with meter marking

Dimensions and specifications may be changed without  prior notice

HELUKABEL®  GmbH . Headquarters . Dieselstraße 8-12 . 71282  Hemmingen  . Germany . Ph. +49 7150  9209-0  . Fax +49 7150  81786  . info@helukabel.de

Our products for renewable energy

GREEN LINE

| Part No | No.cores x cross-sec. mm² | Outer Ø app. mm | Cop. weight kg / km | Weight app. kg / km | Current-carrying capacity [A] at60°C | Conductor resistance Ω / km at 20°C | Sheath colour |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 704225 | 1 | x | 2,5 | 4,5 | 24,0 | 42 | 41 | 8,210 | natural/black |
| 705891 | 1 | x | 2,5 | 4,5 | 24,0 | 42 | 41 | 8,210 | natural/red |
| 705892 | 1 | x | 2,5 | 4,5 | 24,0 | 42 | 41 | 8,210 | natural/blue |
| 704226 | 1 | x | 4 | 5,2 | 38,4 | 60 | 55 | 5,090 | natural/black |
| 705775 | 1 | x | 4 | 5,2 | 38,4 | 60 | 55 | 5,090 | natural/red |
| 705776 | 1 | x | 4 | 5,2 | 38,5 | 60 | 55 | 5,090 | natural/blue |
| 704227 | 1 | x | 6 | 5,9 | 57,6 | 82 | 70 | 3,390 | natural/black |
| 705777 | 1 | x | 6 | 5,9 | 57,6 | 82 | 70 | 3,390 | natural/red |
| 705778 | 1 | x | 6 | 5,9 | 57,6 | 82 | 70 | 3,390 | natural/blue |
| 704228 | 1 | x | 10 | 6,9 | 96,0 | 123 | 98 | 1,950 | natural/black |
| 705893 | 1 | x | 10 | 6,9 | 96,0 | 123 | 98 | 1,950 | natural/red |
| 705894 | 1 | x | 10 | 6,9 | 96,0 | 123 | 98 | 1,950 | natural/blue |
| 704229 | 1 | x | 16 | 8,3 | 153,6 | 190 | 132 | 1,240 | natural/black |
| 706839 | 1 | x | 16 | 8,3 | 153,6 | 190 | 132 | 1,240 | natural/red |
| 706840 | 1 | x | 16 | 8,3 | 153,6 | 190 | 132 | 1,240 | natural/blue |
| 704230 | 1 | x | 25 | 10,0 | 240,0 | 285 | 176 | 0,795 | natural/black |
| 704231 | 1 | x | 35 | 11,0 | 336,0 | 376 | 218 | 0,565 | natural/black |
| 704232 | 1 | x | 50 | 13,0 | 480,0 | 530 | 276 | 0,393 | natural/black |
| 704233 | 1 | x | 70 | 15,3 | 672,0 | 745 | 347 | 0,277 | natural/black |
| 704234 | 1 | x | 95 | 17,0 | 912,0 | 960 | 416 | 0,210 | natural/black |
| 705738 | 1 | x | 120 | 19,1 | 1152,0 | 1220 | 488 | 0,164 | natural/black |
| 705739 | 1 | x | 150 | 22,7 | 1440,0 | 1550 | 566 | 0,132 | natural/black |
| 706288 | 1 | x | 185 | 25,5 | 1776,0 | 1930 | 644 | 0,108 | natural/black |
| 706289 | 1 | x | 240 | 28,3 | 2304,0 | 2550 | 775 | 0,0817 | natural/black |

PV-cables  - male-/fe connecto

adapte

assembly

Dimensions and specifications may be changed without  prior notice

Please accept our offer and let us send you our new brochure. Become aquianted with our complete  Photovoltaic product  range.  Just

use the fax reply.

t

cables &

wires

components

too

Fax  Request

+49 7150 8602

# Text boxes

s

rs

male rs

ls

e